## Worksheet 1
Failure Description |  | Potential consequences to the power system
Secondary functions affected (e.g. protection display flashing) |  | No major consequence. Operator unable to read data from the device’s
display
Intermittent loss of communication in the SCADA system. |  | Possible delay in decision-making by the SCADA system
Protection relay shutdown | The system self-recovers | Substation components unprotected and no communication with the
without operator intervention | SCADA system for approximately one minute
Operator intervention to resume | Substation components unprotected and no communication with the
system’s secondary function | SCADA system for approximately one minute. Operator unable to
read data from the device’s display
Operator intervention to resume | Substation components unprotected and no communication with the
system’s primary function | SCADA system until the operator realize the issue and restarts the
protection system
Operator intervention to resume | Substation components unprotected and no communication with the
system’s primary and secondary | SCADA system until the operator realize the issue and restarts the
functions | protection system. Operator unable to read data from the device’s display