## Worksheet 1
t/ms | Description
20 | In the interval [t/ms=20…30] the frequency is temporarily reduced, as indicated in the zoom of Fig. 14. In other words, at t=20 ms a frequency jump from 50 to 45 Hz takes place. Such a frequency jump is practically invisible in the graph of the time functions, even if you know where it occurs. The change in frequency affects, albeit only slightly, the continuity of the derivatives (slope, curvature …) of the voltage-time curve. If we imagine the sine wave as interpolated by a polynomial, this corresponds to a change in the polynomial coefficients a1,a2,…. The extremely small and therefore invisible change in the polynomial coefficients to the left and right of the discontinuity is sufficient to make it recognizable in the scalogram in Fig. 16 in the form of a wedge.
30 | At t=30 ms another frequency jump back to 50 Hz takes place, combined with a vector jump back to the original fundamental waveform. This is associated with a level jump in the voltage-time curve. In contrast to the frequency jump at t=20 ms, this level jump at t=30 ms is also visible in the time function u(t) at least briefly in the zoomed display. In the scalogram in Fig. 16 of the wavelet transform U(t), however, it is clearly visible again over an increasing time range with the stretching of the wavelet, even over a larger time interval, with the typical wedge shape.
[40...46] | In this interval, the fundamental oscillation of conductor R is superimposed with a broadband noise. The range of values of the noise is about 1 % of the fundamental oscillation amplitude, recognizable in Fig. 15 where the beginning of the time domain is shown enlarged.
[50...56] | Here, in addition to uR(t), uS(t) is also superimposed with a noise, which is obtained from the noise signal of uR using a low-pass filter. The lower bandwidth results in a smaller vertical extent of the green bar in Fig. 16 also for yellow bar in Fig. 17.
[60...66] | Here, the same noise signal is superimposed on the fundamental oscillations of uS and uR . The range of values is again 1 % of the fundamental oscillation amplitude. The high correlation leads to the homogeneous yellow coloration in Fig. 17.
[70...76] | In this interval, uR, uS and uT are each superimposed with a noise signal. The three noise signals of equal magnitude are generated independently of each other, which leads to the inhomogeneous coloring in Fig. 17.
[80...86] | In this interval, uR, uS and uT are superimposed with the same noise signal. The high correlation means that the bar in this interval in Fig. 17 appears largely in shades of gray. Such gray tones are therefore an indication of causes related to the neutral point treatment.